SECTION 07 27 13

SBS MODIFIED BITUMINOUS SHEET VAPOR RETARDERS & AIR BARRIERS

NOTE:  This guide specification is provided as a guideline and must be modified, as required, by the Designer of Record for each project. This specification is prepared in general accordance with CSI format to be included under Division 7 – Thermal and Moisture Protection.  Additional information is provided.  [delete this paragraph]

Optional information is presented in “blue” font below.  Choose appropriate options, delete as necessary.  [delete this paragraph]

- GENERAL

  - SUMMARY

    - Work shall include, but is not limited to, the following:

      - Preparation of existing (new), concrete, steel, wood, gypsum, cementitious wood fiber roof deck, and all flashing substrates.

      - SBS-modified bitumen roof vapor retarder (air barrier).

      - SBS-modified bitumen membrane flashings at penetrations

      - Liquid-applied, reinforced flashings at penetrations.

      - All related materials and labor required to complete specified roofing necessary to receive specified manufacturer’s warranty.

  - RELATED SECTIONS

    - Division 010000 – General Requirements

    - Division 011000 – Summary of Work

    - Division 072200 – Roof Insulation

    - Division 075213 – Atactic Polypropylene (APP) Modified Bitumen Membrane Roofing

    - Division 075216 – Styrene-Butadiene-Styrene (SBS) Modified Bitumen Membrane Roofing

    - Division 076200 – Sheet Metal Flashing and Trim

  - DEFINITIONS

    - ASTM D 1079-Definitions of Term Relating to Roofing and Waterproofing.

    - The National Roofing Contractors Association (NRCA) Roofing and Waterproofing Manual, Fifth Edition Glossary.

  - REFERENCES

    - AMERICAN SOCIETY OF CIVIL ENGINEERS - Reference Document ASCE 7, Minimum Design Loads for Buildings and Other Structures.

    - AMERICAN STANDARD OF TESTING METHODS (ASTM):

      - ASTM C 836 - Standard Specification for High Solids Content, Cold Liquid-Applied Elastomeric Waterproofing Membrane for Use with Separate Wearing Course.

      - ASTM C 920 - Standard Specification for Elastomeric Joint Sealants

      - ASTM D 41 - Standard Specification for Asphalt Primer Used in Roofing, Damp proofing, and Waterproofing.

      - ASTM D 312- Standard Specification for Asphalt Used in Roofing.

      - ASTM D 1970 - Standard Specification for Self-Adhering Polymer Modified Bituminous Sheet Materials Used as Steep Roofing Underlayment for Ice Dam Protection.

      - ASTM D 2178 - Standard Specification for Asphalt Glass Felt Used in Roofing and Waterproofing.

      - ASTM D 3019 - Standard Specification for Lap Cement Used with Asphalt Roll Roofing, Non-Fibered, Asbestos-Fibered, and Non-Asbestos-Fibered.

      - ASTM D 3746 - Standard Test Method for Impact Resistance of Bituminous Roofing System.

      - ASTM D 4586 - Standard Specification for Asphalt Roof Cement, Asbestos-Free.

      - ASTM D 4601 - Standard Specification for Asphalt-Coated Glass Fiber Base Sheet Used in Roofing.

      - ASTM D 5147 - Standard Test Methods for Sampling and Testing Modified Bituminous Sheet Material.

      - ASTM D 5849 - Standard Test Method for Evaluating Resistance of Modified Bituminous Roofing Membrane to Cyclic Fatigue (Joint Displacement)

      - ASTM D 6163 - Standard Specification for Styrene Butadiene Styrene (SBS) Modified Bituminous Sheet Materials Using Glass Fiber Reinforcements.

      - ASTM D 6164 - Standard Specification for Styrene Butadiene Styrene (SBS) Modified Bituminous Sheet Materials Using Polyester Reinforcements.

      - ASTM D 6222 - Standard Specification for Atactic Polypropylene (APP) Modified Bituminous Sheet Materials Using a Polyester Reinforcement.

      - ASTM D 6223 - Standard Specification for Atactic Polypropylene (APP) Modified Bituminous Sheet Materials Using a Combination of Polyester and Glass Fiber Reinforcements

      - ASTM D 6509 – Standard Specification for Atactic Polyproylene (APP) Modified Bituminous Base Sheet Materials Using Glass Fiber Reinforcements.

      - ASTM D 7379 - Standard Test Methods for Strength of Modified Bitumen Sheet Material Laps Using Cold Process Adhesive.

      - ASTM E 108 - Standard Test Methods for Fire Tests of Roof Coverings.

    - AMERICAN NATIONAL STANDARDS INSTITUTE (ANSI)::

      - ANSI/SPRI FX-1, Standard Field Test Procedure for Determining the Withdrawal Resistance of Roofing Fasteners.

      - ANSI/FM 4474- American National Standard for Evaluating the Simulated Wind Resistance of Roof Assemblies Using Static Positive and/or Negative Differential Pressures.

    - CANADIAN GENERAL STANDARDS BOARD (CGSB):

      - CGSB 37-GP 56M- Standard for: Modified Bituminous, Prefabricated, and Reinforced for Roofing.

    - FACTORY MUTUAL (FM):

      - FM 4450 - Approval Standard - Class I Insulated Steel Roof Decks.

      - FM 4470 - Approval Standard - Class I Roof Covers.

    - FLORIDA BUILDING CODE (FBC):

      - 20XX Florida Building Code (FBC).

    - INTERNATIONAL CODES COUNCIL (ICC):

      - 20XX International Building Code (IBC).

    - NATIONAL ROOFING CONTRACTORS ASSOCIATION (NRCA).

    - UNDERWRITERS LABORATORY (UL):

      - UL 790 Standard Test Methods for Fire Tests of Roof Coverings.

      - UL 1256 – Fire Test of Roof Deck Constructions.

  - ACTION SUBMITTALS

    - Product Data Sheets: Submit manufacturer’s product data sheets, installation instructions and/or general requirements for each component.

    - Safety Data Sheets: Submit manufacturer’s Safety Data Sheets (SDS) for each component.

    - Sample/Specimen Warranty from the manufacturer and contractor.

    - Shop Drawings: Provide roof plan and applicable roof system detail drawings.

  - INFORMATIONAL SUBMITTALS

    - Contractor Certification: Submit written certification from roofing system manufacturer certifying that the applicator is authorized by the manufacturer to install the specified materials and system.

  - CLOSEOUT SUBMITTALS

    - Warranty: Provide manufacturer’s and contractor’s warranties upon substantial completion of the roofing system.

  - QUALITY ASSURANCE

    - MANUFACTURER QUALIFICATIONS:

      - Manufacture shall have 20 years of experience manufacturing modified bitumen roofing materials.

    - CONTRACTOR QUALIFICATIONS:

      - Contractor shall be authorized by the manufacturer to install specified materials prior to the bidding period through satisfactory project completion.

      - Applicators shall have completed projects of similar scope using same materials as specified herein.

      - Contractor shall provide full time, on-site superintendent or foreman experienced with the specified roof system through satisfactory project completion.

      - Applicators shall be skilled in the application methods for all materials.

      - Contractor shall maintain a daily record, on-site, documenting material installation and related project conditions.

      - Contractor shall maintain a copy of all submittal documents, on-site, available at all times for reference.

  - DELIVERY, STORAGE AND HANDLING

    - Refer to each product data sheet or other published literature for specific requirements.

    - Deliver materials and store them in their unopened, original packaging, bearing the manufacturer's name, related standards, and any other specification or reference accepted as standard.

    - Protect and store materials in a dry, well-vented, and weatherproof location. Only materials to be used the same day shall be removed from this location. During cold weather, store materials in a heated location, removed only as needed for immediate use.

    - When materials are to be stored outdoors, store away from standing water, stacked on raised pallets or dunnage, at least 4 in or more above ground level.  Carefully cover storage with “breathable” tarpaulins to protect materials from precipitation and to prevent exposure to condensation.

    - Carefully store roof membrane materials delivered in rolls on-end with selvage edges up.  Store and protect roll storage to prevent damage.

    - Properly dispose of all product wrappers, pallets, cardboard tubes, scrap, waste, and debris.  All damaged materials shall be removed from job site and replaced with new, suitable materials.

  - SITE CONDITIONS

    - SAFETY:

      - The contractor shall be responsible for complying with all project-related safety and environmental requirements.

      - Heat-welding shall include heating the specified membrane ply using propane roof torches or electric hot-air welding equipment.  The contractor shall determine when and where conditions are appropriate to utilize heat-welding equipment.  When conditions are determined by the contractor to be unsafe to proceed, equivalent SBS-modified bitumen materials and methods shall be utilized to accommodate requirements and conditions.

      - Refer to NRCA CERTA recommendations, local codes and building owner’s requirements for hot work operations.

      - The contractor shall review project conditions and determine when and where conditions are appropriate to utilize the specified liquid-applied, or semi-solid roofing materials.  When conditions are determined by the contractor to be unsafe or undesirable to proceed, measures shall be taken to prevent or eliminate the unsafe or undesirable exposures and conditions, or equivalent approved materials and methods shall be utilized to accommodate requirements and conditions.

      - The contractor shall review project conditions and determine when and where conditions are appropriate to utilize the specified hot asphalt-applied materials.  When conditions are determined by the contractor to be unsafe or undesirable to proceed, measures shall be taken to prevent or eliminate the unsafe or undesirable exposures and conditions, or equivalent approved materials and methods shall be utilized to accommodate requirements and conditions. .

      - The contractor shall refer to product Safety Data Sheets (SDS) for health, safety, and environment related hazards, and take all necessary measures and precautions to comply with exposure requirements.

    - ENVIRONMENTAL CONDITIONS:

      - Monitor substrate temperature and material temperature, as well as all environmental conditions such as ambient temperature, moisture, sun, cloud cover, wind, humidity, and shade.  Ensure conditions are satisfactory to begin work and ensure conditions remain satisfactory during the installation of specified materials.  Materials and methods shall be adjusted as necessary to accommodate varying project conditions.  Materials shall not be installed when conditions are unacceptable to achieve the specified results.

      - Precipitation and dew point:  Monitor weather to ensure the project environment is dry before, and will remain dry, during the application of roofing materials.   Ensure all roofing materials and substrates remain above the dew point temperature as required to prevent condensation and maintain dry conditions.

      - Mopping asphalt application:  Primer, where used, shall be fully dry before applying hot asphalt.  Take all necessary measures and monitor all conditions, to ensure the specified asphalt temperature is no less than 400(F (204(C) at the point of contact with the specified membrane as it is rolled into the hot asphalt.

      - Cold adhesive application:  Primer, where used, shall be fully dry before proceeding.  During cold weather, store the specified membrane adhesives, flashing cements and mastics in heated storage areas.  Take all necessary measures and monitor application conditions, to ensure the adhesive and cement materials are no less than 70(F (21(C) at the point of contact with the membrane.

      - Self-adhesive membrane application:  During cold weather, store the specified self-adhesive membrane and primer materials in heated storage areas to ensure materials remain no less than 70(F (21(C) during application.  Ensure conditions allow primer to remain tacky, but not wet so that primer will transfer to finger when touched.  Self-adhered primer should not fully dry and lose tack before applying the self-adhesive membrane.  Ensure conditions remain satisfactory to achieve membrane adhesion as specified.

      - Heat-Welding Application:  Take all necessary precautions and measures to monitor conditions to ensure all environmental conditions are safe to proceed with the use of torches and hot-air welding equipment.   Combustibles, flammable liquids and solvent vapors that represent a hazard shall be eliminated and primers shall be fully dry before proceeding with heat-welding operations. Refer to NRCA CERTA recommendations.

  - PERFORMANCE REQUIREMENTS

    - FIRE CLASSIFICATION:

      - Vapor Retarder/Air Barrier included in system performance testing in accordance with UL 790, ASTM E108, FM 4450 or FM 4470.

        - Meets requirements of UL Class A or FM Class A.

      - Vapor Retarder/Air Barrier included in system performance testing in accordance with UL 1256, FM 4450 or FM 4470 to meet the specified requirements for interior flame spread and fuel contribution.

        - Meets requirements of UL 1256, or FM Class 1.

  - WARRANTY

    - Vapor Retarder/Air Barrier shall be included in the specified roofing Manufacturer's No Dollar Limit (NDL) Warranty.  The Vapor Retarder/Air Barrier manufacturer shall provide the owner with the manufacturer’s warranty for 10 15 20 years from the date the warranty is issued.

    - The contractor shall guarantee the workmanship and shall provide the owner with the contractor’s warranty covering workmanship for a period of 2 years from completion date.

- PRODUCTS

  - MANUFACTURER

    - PRODUCT QUALITY ASSURANCE PROGRAM: Manufacturer shall be an ISO 9001 registered company. A ‘Quality Compliance Certificate (QCC) for reporting/confirming the tested values of the SBS-Modified Bitumen Membrane Materials will be supplied upon request.

    - ACCEPTABLE MANUFACTURER:

      - PERFORMANCE ROOF SYSTEMS, INC., A SOPREMA GROUP COMPANY, located at: 4800 Dr. Martin Luther King Jr. Blvd., Kansas City, MO  64130; Tel: 816-921-0221; Tel 800-727-9872; Website: www.performanceroofsystems.us

      - Acceptable Alternate Manufacturers:  _________________________

  - MODIFIED BITUMEN VAPOR RETARDER

    - VAPOR RETARDER, HEAT-WELDED:

        - DERBIBASE: High quality smooth surfaced APP Modified Bitumen Roofing Membrane designed to act as a base or ply sheet. Meets or exceeds ASTM D6509, per ASTM D5147 test methods:

          - Thickness, min, mm [mils]: 2.0 [80]

          - Width: 39 3/8 in [1.0 m]

          - Length: 66ft 5 in [20.1m]

          - Weight: 94 lb [42.6 kg]

          - Net Coverage: 200ft2 [18.6 m2]

          - Net mass/unit area, min, g/m2 [lbs/100 ft2]: [49 lbs/100 ft2]

          - Bottom coating thickness, heat welding application products, min, mm [mils]: N/A

          - Peak Load at -18 ± 2°C [0 ± 3.6°F], MD and XMD, min, kN/m [lbf/in.]:

            - MD 166 lbf/in; XMD 141 lbf/in

          - Elongation at -18 ± 2°C [0 ± 3.6°F], MD and XMD at peak load, min, %: MD 4.4 %; XMD: 4.8 %

          - Peak Load at 23 ± 2°C [73.4 ± 3.6°F], MD and XMD, before and after heat conditioning, min, kN/m [lbf/in.]:

            - Before: MD 108 lbf/in, XMD 82 lbf/in

            - After: MD 114 lbf/in, XMD 100 lbf/in

          - Elongation at 23 ± 2°C [73.4 ± 3.6°F], MD and XMD at peak load, before and after heat conditioning, min, %:

            - Before: MD 4.0 %; XMD: 4.1 %

            - After: MD 3.8 %; XMD: 4.1 %

          - Tear Strength at 23 ± 2°C [73.4 ± 3.6°F], min, N[lbf]: MD 127 lbf; XMD 103 lbf

          - Low Temperature, flexibility, before and after heat conditioning, max, °C [°F]:

            - Before: 32°F

            - After: 32°F

          - Dimensional stability, max, %: MD 0.0%; XMD: 0.0%

          - Compound stability, min, °C [°F]: 230°F

          - Water absorption, max, %: 1.2%

          - Moisture content, max, %: 0.4%

          - Low temperature unrolling, max, °C [°F]: Pass

        - DERBIBASE ULTRA: High quality smooth surfaced APP Modified Bitumen Roofing Membrane designed to act as a base or ply sheet. Meets or exceeds ASTM D6509, per ASTM D5147 test methods:

          - Thickness, min, mm [mils]: 3.0mm [120 mils]

          - Width: 39 3/8 in [1.0 m]

          - Length: 49ft 6 in [15m]

          - Weight: 108 lb [48.9 kg]

          - Net Coverage: 150ft2 [13.9 m2]

          - Net mass/unit area, min, g/m2 [lbs/100 ft2]: [63 lbs/100 ft2]

          - Bottom coating thickness, heat welding application products, min, mm [mils]: 60 mils

          - Peak Load at -18 ± 2°C [0 ± 3.6°F], MD and XMD, min, kN/m [lbf/in.]:

            - MD 166 lbf/in; XMD 141 lbf/in

          - Elongation at -18 ± 2°C [0 ± 3.6°F], MD and XMD at peak load, min, %: MD 4.4 %; XMD: 4.8 %

          - Peak Load at 23 ± 2°C [73.4 ± 3.6°F], MD and XMD, before and after heat conditioning, min, kN/m [lbf/in.]:

            - Before: MD 108 lbf/in, XMD 82 lbf/in

            - After: MD 118 lbf/in, XMD 105 lbf/in

          - Elongation at 23 ± 2°C [73.4 ± 3.6°F], MD and XMD at peak load, before and after heat conditioning, min, %:

            - Before: MD 4.0 %; XMD: 4.1 %

            - After: MD 3.8 %; XMD: 4.1 %

          - Tear Strength at 23 ± 2°C [73.4 ± 3.6°F], min, N[lbf]: MD 127 lbf; XMD 103 lbf

          - Low Temperature, flexibility, before and after heat conditioning, max, °C [°F]:

            - Before: 32°F

            - After: 32°F

          - Dimensional stability, max, %: MD 0.0%; XMD: 0.0%

          - Compound stability, min, °C [°F]: 230°F

          - Water absorption, max, %: 1.2%

          - Moisture content, max, %: 0.4%

          - Low temperature unrolling, max, °C [°F]: Pass

        - DERBIGUM P: High quality smooth surfaced APP Modified Bitumen Roofing Membrane designed to act as a base or ply sheet. Meets or exceeds ASTM D6222, per ASTM D5147 test methods:

          - Thickness, min, mm [mils]: 4.0 mm [160 mils]

          - Width: 39 3/8 in [1.0 m]

          - Length: 33 ft 6in [10.2m]

          - Weight: 100lb [45 kg]

          - Net Coverage: 100ft2 [9m2]

          - Net mass/unit area, min, g/m2 [lbs/100 ft2]: 86 lbs/100 ft2

          - Bottom coating thickness, heat welding application products, min, mm [mils]: 35 mils

          - Peak Load at 23 ± 2°C [73.4 ± 3.6°F], MD and XMD, before and after heat conditioning, min, kN/m [lbf/in.]:

            - Before: MD 80 lbf/in; XMD 60 lbf/in

            - After: MD 84 lbf/in; XMD 52 lbf/in

          - Elongation at 23 ± 2°C [73.4 ± 3.6°F], MD and XMD at peak load, before and after heat conditioning, min, %:

            - Before: MD 37 %; XMD 45 %

            - After: MD 36 %; XMD 40 %

          - Peak Load at -18 ± 2°C [0 ± 3.6°F], MD and XMD, min, kN/m [lbf/in.]: MD 104 lbf/in; XMD 88 lbf/in

          - Elongation at -18 ± 2°C [0 ± 3.6°F], MD and XMD, at peak load, min, %: MD 12%; XMD 10%

          - Ultimate elongation at 23 ± 2°C [73.4 ± 3.6°F], MD and XMD, min, %: MD 42%; XMD 55%

          - Tear Strength at 23 ± 2°C [73.4 ± 3.6°F], min, N[lbf]: MD 150 lbf; XMD 95 lbf

          - Low Temperature, flexibility, before and after heat conditioning, max, °C [°F]:

            - Before: Pass

            - After: Pass

          - Dimensional stability, max, %: MD 0.1%; XMD 0.2%

          - Compound stability, min, °C [°F]: Pass

          - Water absorption, max, %: 1.8%

          - Moisture content, max, %: 0.3 %

          - Low temperature unrolling, max, °C [°F]: Pass

        - DERBIGUM GP: High quality smooth surfaced APP Modified Bitumen Roofing Membrane. Meets or exceeds ASTM D6223, per ASTM D5147 test methods:

          - Thickness, min, mm [mils]:160 mil

          - Width: 39 3/8 In [1.0 m]

          - Length: 33 ft  6 in [10.2m]

          - Weight: 94 lb [42.6kg]

          - Net Coverage: 100 ft2 [9.2 m2]

          - Net mass/unit area, min, g/m2 [lbs/100 ft2]: 84 lbs/100 ft2

          - Bottom coating thickness, heat welding application products, min, mm [mils]: 89 mils

          - Peak Load at 23 ± 2°C [73.4 ± 3.6°F], MD and XMD, before and after heat conditioning, min, kN/m [lbf/in.]:

            - Before: MD 144 lbf/in; XMD 105 lbf/in

            - After: MD 118 lbf/in; XMD 118 lbf/in

          - Elongation at 23 ± 2°C [73.4 ± 3.6°F], MD and XMD at peak load, before and after heat conditioning, min, %:

            - Before: MD 4%; XMD 4%

            - After: MD 4%; XMD 4%

          - Peak Load at -18 ± 2°C [0 ± 3.6°F], MD and XMD, min, kN/m [lbf/in.]: MD 235 lbf/in; XMD 193 lbf/in

          - Elongation at -18 ± 2°C [0 ± 3.6°F], MD and XMD, at peak load, min, %: MD 5%; XMD 5%

          - Tear Strength at 23 ± 2°C [73.4 ± 3.6°F], min, N[lbf]: MD 198 lbf; XMD 178 lbf

          - Low Temperature, flexibility, before and after heat conditioning, max, °C [°F]:

            - Before: PASS

            - After: PASS

          - Dimensional stability, max, %: MD -0.2%; XMD 0%

          - Compound stability, min, °C [°F]: PASS

          - Water absorption, max, %: 3.2%

          - Moisture content, max, %: 0.2%

          - Low temperature unrolling, max, °C [°F]: PASS

        - DERBIGUM XPS: High quality smooth surfaced APP Modified Bitumen Roofing Membrane. Meets or exceeds ASTM D6223, per ASTM D5147 test methods:

          - Thickness, min, mm [mils]:160 mil

          - Width: 39 3/8 In [1.0 m]

          - Length: 33 ft  6 in [10.2m]

          - Weight: 97 lb [42.6kg]

          - Net Coverage: 100 ft2 [9.2 m2]

          - Net mass/unit area, min, g/m2 [lbs/100 ft2]: 86 lbs/100 ft2

          - Bottom coating thickness, heat welding application products, min, mm [mils]: 92 mils

          - Peak Load at 23 ± 2°C [73.4 ± 3.6°F], MD and XMD, before and after heat conditioning, min, kN/m [lbf/in.]:

            - Before: MD 197 lbf/in; XMD 185 lbf/in

            - After: NT

          - Elongation at 23 ± 2°C [73.4 ± 3.6°F], MD and XMD at peak load, before and after heat conditioning, min, %:

            - Before: MD 5%; XMD 5%

            - After: NT

          - Peak Load at -18 ± 2°C [0 ± 3.6°F], MD and XMD, min, kN/m [lbf/in.]: NT

          - Elongation at -18 ± 2°C [0 ± 3.6°F], MD and XMD, at peak load, min, %: NT

          - Tear Strength at 23 ± 2°C [73.4 ± 3.6°F], min, N[lbf]: MD 270 lbf; XMD 324 lbf

          - Low Temperature, flexibility, before and after heat conditioning, max, °C [°F]:

            - Before: PASS

            - After: PASS

          - Dimensional stability, max, %: NT

          - Compound stability, min, °C [°F]: PASS

          - Water absorption, max, %: N/A

          - Moisture content, max, %: N/A

          - Low temperature unrolling, max, °C [°F]: NT

        - DERBICOLOR P: High quality granule surfaced APP Modified Bitumen Roofing Membrane designed to act as a base or ply sheet. Meets or exceeds ASTM D6222, per ASTM D5147 test methods:

          - Thickness, min, mm [mils]: 4.1 mm [161 mils]

          - Width: 39 3/8 in [1.0 m]

          - Length: 33 ft 6in [10.2m]

          - Weight: 105lb [47.6 kg]

          - Net Coverage: 100ft2 [9m2]

          - Net mass/unit area, min, g/m2 [lbs/100 ft2]: 102 lbs/100 ft2

          - Bottom coating thickness, heat welding application products, min, mm [mils]: 45 mils

          - Peak Load at 23 ± 2°C [73.4 ± 3.6°F], MD and XMD, before and after heat conditioning, min, kN/m [lbf/in.]:

            - Before: MD 71 lbf/in; XMD 50 lbf/in

            - After: MD 67 lbf/in; XMD 50 lbf/in

          - Elongation at 23 ± 2°C [73.4 ± 3.6°F], MD and XMD at peak load, before and after heat conditioning, min, %:

            - Before: MD 49%; XMD 67%

            - After: MD 45 %; XMD 63%

          - Peak Load at -18 ± 2°C [0 ± 3.6°F], MD and XMD, min, kN/m [lbf/in.]: MD 76; XMD 61

          - Elongation at -18 ± 2°C [0 ± 3.6°F], MD and XMD, at peak load, min, %: MD 21%; XMD 15%

          - Ultimate elongation at 23 ± 2°C [73.4 ± 3.6°F], MD and XMD, min, %: MD 54 lbf/in; XMD 72 lbf/in

          - Tear Strength at 23 ± 2°C [73.4 ± 3.6°F], min, N[lbf]: MD 122 lbf; XMD 75 lbf

          - Low Temperature, flexibility, before and after heat conditioning, max, °C [°F]:

            - Before: Pass

            - After: Pass

          - Dimensional stability, max, %: MD 0.1%; XMD 0.1%

          - Compound stability, min, °C [°F]: Pass

          - Water absorption, max, %: 1.1%

          - Moisture content, max, %: 0.2 %

          - Low temperature unrolling, max, °C [°F]: Pass

    - VAPOR RETARDER, SELF-ADHERED:

      - DERBISTICK SA: SBS-modified bitumen self-adhered vapor retarder, air barrier membrane with release film on the bottom surface and a tri-laminate woven polyethylene film top surface reinforcement.

        - Thickness: 31.5 mils (0.80 mm)

        - Width: 45 in (1.14 m)

        - Length: 133 ft (40.8 m)

        - Meets or exceeds ASTM D2178 “Standard Test Method for Air Permeance of Building Materials.”

        - Meets or exceeds ASTM E96 (Procedure B) “Standard Test method for Water Vapor Transmission of Materials.”

        - Meets or exceeds UL 1256 for direct to steel deck applications in accordance with UL Construction No. 123.

      - DERBIBASE SA ULTRA: SBS-modified bitumen, self-adhesive membrane with release film on the bottom surface and a sanded top surface.  Non-woven polyester reinforced. Meets or exceeds ASTM D6164, Type I, Grade S, per ASTM D5147 test methods:

          - Thickness: 98 mils (2.5 mm)

          - Width: 39.4 in (1 m)

          - Length: 49.2 ft (15 m)

          - Roll weight: 103 lb (46.5 kg)

          - Net mass per unit area, lb/100 sq ft (g/sq m):

            - 63 lb (3098 g)

          - Peak load @ 0(F (-18(C), lbf/in (kN/m).

            - MD 110 lbf/in (19.3 kN/m), XMD 85 lbf/in (14.9 kN/m)

          - Elongation at peak load @ 0(F (-18(C), lbf/in (kN/m):

            - MD 35%, XMD 40%

          - Peak load @ 73.4(F (23(C), lbf/in (kN/m):

            - MD 85 lbf/in (14.9 kN/m), XMD 65 lbf/in (11.4 kN/m)

          - Elongation at peak load @ 73.4(F (23(C), lbf/in (kN/m):

            - MD 55%, XMD 60%

          - Ultimate Elongation @ 73.4(F (23(C), lbf/in (kN/m):

            - MD 60%, XMD 65%

          - Tear Strength @ 73.4(F (23(C), lbf (N):

            - MD 125 lbf (556 N), XMD 85 lbf (378 N)

          - Low temperature flexibility, (F ((C):

            - MD/XMD:  -15(F (-26(C)

          - Dimensional stability, %:

            - MD/XMD: Less than 0.5%

          - Compound stability, (F ((C):

            - MD/XMD: 240(F (116(C):

      - DERBIBASE SA: SBS-modified bitumen, self-adhesive membrane with release film on the bottom surface and a sanded top surface.  Glass fiber reinforcement. Meets or exceeds ASTM D6163, Type I, Grade S, per ASTM D5147 test methods:

          - Thickness: 87 mils (2.2 mm)

          - Width: 39.4 in (1 m)

          - Length: 49.2 ft (15 m)

          - Roll weight: 73 lb (33.3 kg)

          - Net mass per unit area, lb/100 sq ft (g/sq m):

            - 45.5 lb (2220 g)

          - Peak load @ 0(F (-18(C), lbf/in (kN/m).

            - MD 100 lbf/in (17.5 kN/m), XMD 90 lbf/in (15.8 kN/m)

          - Elongation at peak load @ 0(F (-18(C), lbf/in (kN/m):

            - MD 4%, XMD 4%

          - Peak load @ 73.4(F (23(C), lbf/in (kN/m):

            - MD 50 lbf/in (8.8 kN/m), XMD 40 lbf/in (7.0 kN/m)

          - Elongation at peak load @ 73.4(F (23(C), lbf/in (kN/m):

            - MD 5%, XMD 4%

          - Ultimate Elongation @ 73.4(F (23(C), lbf/in (kN/m):

            - MD 45%, XMD 45%

          - Tear Strength @ 73.4(F (23(C), lbf (N):

            - MD 60 lbf (267 N), XMD 60 lbf (267 N)

          - Low temperature flexibility, (F ((C):

            - MD/XMD:  -15(F (-26(C)

          - Dimensional stability, %:

            - MD/XMD: Less than 0.1%

          - Compound stability, (F ((C):

            - MD/XMD: 250(F (121(C)

    - VAPOR RETARDER, COLD ADHESIVE

        - DERBIBASE: High quality smooth surfaced APP Modified Bitumen Roofing Membrane designed to act as a base or ply sheet. Meets or exceeds ASTM D6509, per ASTM D5147 test methods:

          - Thickness, min, mm [mils]: 2.0 [80]

          - Width: 39 3/8 in [1.0 m]

          - Length: 66ft 5 in [20.1m]

          - Weight: 94 lb [42.6 kg]

          - Net Coverage: 200ft2 [18.6 m2]

          - Net mass/unit area, min, g/m2 [lbs/100 ft2]: [49 lbs/100 ft2]

          - Bottom coating thickness, heat welding application products, min, mm [mils]: N/A

          - Peak Load at -18 ± 2°C [0 ± 3.6°F], MD and XMD, min, kN/m [lbf/in.]:

            - MD 166 lbf/in; XMD 141 lbf/in

          - Elongation at -18 ± 2°C [0 ± 3.6°F], MD and XMD at peak load, min, %: MD 4.4 %; XMD: 4.8 %

          - Peak Load at 23 ± 2°C [73.4 ± 3.6°F], MD and XMD, before and after heat conditioning, min, kN/m [lbf/in.]:

            - Before: MD 108 lbf/in, XMD 82 lbf/in

            - After: MD 114 lbf/in, XMD 100 lbf/in

          - Elongation at 23 ± 2°C [73.4 ± 3.6°F], MD and XMD at peak load, before and after heat conditioning, min, %:

            - Before: MD 4.0 %; XMD: 4.1 %

            - After: MD 3.8 %; XMD: 4.1 %

          - Tear Strength at 23 ± 2°C [73.4 ± 3.6°F], min, N[lbf]: MD 127 lbf; XMD 103 lbf

          - Low Temperature, flexibility, before and after heat conditioning, max, °C [°F]:

            - Before: 32°F

            - After: 32°F

          - Dimensional stability, max, %: MD 0.0%; XMD: 0.0%

          - Compound stability, min, °C [°F]: 230°F

          - Water absorption, max, %: 1.2%

          - Moisture content, max, %: 0.4%

          - Low temperature unrolling, max, °C [°F]: Pass

        - DERBIBASE ULTRA: High quality smooth surfaced APP Modified Bitumen Roofing Membrane designed to act as a base or ply sheet. Meets or exceeds ASTM D6509, per ASTM D5147 test methods:

          - Thickness, min, mm [mils]: 3.0mm [120 mils]

          - Width: 39 3/8 in [1.0 m]

          - Length: 49ft 6 in [15m]

          - Weight: 108 lb [48.9 kg]

          - Net Coverage: 150ft2 [13.9 m2]

          - Net mass/unit area, min, g/m2 [lbs/100 ft2]: [63 lbs/100 ft2]

          - Bottom coating thickness, heat welding application products, min, mm [mils]: 60 mils

          - Peak Load at -18 ± 2°C [0 ± 3.6°F], MD and XMD, min, kN/m [lbf/in.]:

            - MD 166 lbf/in; XMD 141 lbf/in

          - Elongation at -18 ± 2°C [0 ± 3.6°F], MD and XMD at peak load, min, %: MD 4.4 %; XMD: 4.8 %

          - Peak Load at 23 ± 2°C [73.4 ± 3.6°F], MD and XMD, before and after heat conditioning, min, kN/m [lbf/in.]:

            - Before: MD 108 lbf/in, XMD 82 lbf/in

            - After: MD 118 lbf/in, XMD 105 lbf/in

          - Elongation at 23 ± 2°C [73.4 ± 3.6°F], MD and XMD at peak load, before and after heat conditioning, min, %:

            - Before: MD 4.0 %; XMD: 4.1 %

            - After: MD 3.8 %; XMD: 4.1 %

          - Tear Strength at 23 ± 2°C [73.4 ± 3.6°F], min, N[lbf]: MD 127 lbf; XMD 103 lbf

          - Low Temperature, flexibility, before and after heat conditioning, max, °C [°F]:

            - Before: 32°F

            - After: 32°F

          - Dimensional stability, max, %: MD 0.0%; XMD: 0.0%

          - Compound stability, min, °C [°F]: 230°F

          - Water absorption, max, %: 1.2%

          - Moisture content, max, %: 0.4%

          - Low temperature unrolling, max, °C [°F]: Pass

        - DERBIGUM P: High quality smooth surfaced APP Modified Bitumen Roofing Membrane designed to act as a base or ply sheet. Meets or exceeds ASTM D6222, per ASTM D5147 test methods:

          - Thickness, min, mm [mils]: 4.0 mm [160 mils]

          - Width: 39 3/8 in [1.0 m]

          - Length: 33 ft 6in [10.2m]

          - Weight: 100lb [45 kg]

          - Net Coverage: 100ft2 [9m2]

          - Net mass/unit area, min, g/m2 [lbs/100 ft2]: 86 lbs/100 ft2

          - Bottom coating thickness, heat welding application products, min, mm [mils]: 35 mils

          - Peak Load at 23 ± 2°C [73.4 ± 3.6°F], MD and XMD, before and after heat conditioning, min, kN/m [lbf/in.]:

            - Before: MD 80 lbf/in; XMD 60 lbf/in

            - After: MD 84 lbf/in; XMD 52 lbf/in

          - Elongation at 23 ± 2°C [73.4 ± 3.6°F], MD and XMD at peak load, before and after heat conditioning, min, %:

            - Before: MD 37 %; XMD 45 %

            - After: MD 36 %; XMD 40 %

          - Peak Load at -18 ± 2°C [0 ± 3.6°F], MD and XMD, min, kN/m [lbf/in.]: MD 104 lbf/in; XMD 88 lbf/in

          - Elongation at -18 ± 2°C [0 ± 3.6°F], MD and XMD, at peak load, min, %: MD 12%; XMD 10%

          - Ultimate elongation at 23 ± 2°C [73.4 ± 3.6°F], MD and XMD, min, %: MD 42%; XMD 55%

          - Tear Strength at 23 ± 2°C [73.4 ± 3.6°F], min, N[lbf]: MD 150 lbf; XMD 95 lbf

          - Low Temperature, flexibility, before and after heat conditioning, max, °C [°F]:

            - Before: Pass

            - After: Pass

          - Dimensional stability, max, %: MD 0.1%; XMD 0.2%

          - Compound stability, min, °C [°F]: Pass

          - Water absorption, max, %: 1.8%

          - Moisture content, max, %: 0.3 %

          - Low temperature unrolling, max, °C [°F]: Pass

        - DERBIGUM GP: High quality smooth surfaced APP Modified Bitumen Roofing Membrane. Meets or exceeds ASTM D6223, per ASTM D5147 test methods:

          - Thickness, min, mm [mils]:160 mil

          - Width: 39 3/8 In [1.0 m]

          - Length: 33 ft  6 in [10.2m]

          - Weight: 94 lb [42.6kg]

          - Net Coverage: 100 ft2 [9.2 m2]

          - Net mass/unit area, min, g/m2 [lbs/100 ft2]: 84 lbs/100 ft2

          - Bottom coating thickness, heat welding application products, min, mm [mils]: 89 mils

          - Peak Load at 23 ± 2°C [73.4 ± 3.6°F], MD and XMD, before and after heat conditioning, min, kN/m [lbf/in.]:

            - Before: MD 144 lbf/in; XMD 105 lbf/in

            - After: MD 118 lbf/in; XMD 118 lbf/in

          - Elongation at 23 ± 2°C [73.4 ± 3.6°F], MD and XMD at peak load, before and after heat conditioning, min, %:

            - Before: MD 4%; XMD 4%

            - After: MD 4%; XMD 4%

          - Peak Load at -18 ± 2°C [0 ± 3.6°F], MD and XMD, min, kN/m [lbf/in.]: MD 235 lbf/in; XMD 193 lbf/in

          - Elongation at -18 ± 2°C [0 ± 3.6°F], MD and XMD, at peak load, min, %: MD 5%; XMD 5%

          - Tear Strength at 23 ± 2°C [73.4 ± 3.6°F], min, N[lbf]: MD 198 lbf; XMD 178 lbf

          - Low Temperature, flexibility, before and after heat conditioning, max, °C [°F]:

            - Before: PASS

            - After: PASS

          - Dimensional stability, max, %: MD -0.2%; XMD 0%

          - Compound stability, min, °C [°F]: PASS

          - Water absorption, max, %: 3.2%

          - Moisture content, max, %: 0.2%

          - Low temperature unrolling, max, °C [°F]: PASS

        - DERBIGUM XPS: High quality smooth surfaced APP Modified Bitumen Roofing Membrane. Meets or exceeds ASTM D6223, per ASTM D5147 test methods:

          - Thickness, min, mm [mils]:160 mil

          - Width: 39 3/8 In [1.0 m]

          - Length: 33 ft  6 in [10.2m]

          - Weight: 97 lb [42.6kg]

          - Net Coverage: 100 ft2 [9.2 m2]

          - Net mass/unit area, min, g/m2 [lbs/100 ft2]: 86 lbs/100 ft2

          - Bottom coating thickness, heat welding application products, min, mm [mils]: 92 mils

          - Peak Load at 23 ± 2°C [73.4 ± 3.6°F], MD and XMD, before and after heat conditioning, min, kN/m [lbf/in.]:

            - Before: MD 197 lbf/in; XMD 185 lbf/in

            - After: NT

          - Elongation at 23 ± 2°C [73.4 ± 3.6°F], MD and XMD at peak load, before and after heat conditioning, min, %:

            - Before: MD 5%; XMD 5%

            - After: NT

          - Peak Load at -18 ± 2°C [0 ± 3.6°F], MD and XMD, min, kN/m [lbf/in.]: NT

          - Elongation at -18 ± 2°C [0 ± 3.6°F], MD and XMD, at peak load, min, %: NT

          - Tear Strength at 23 ± 2°C [73.4 ± 3.6°F], min, N[lbf]: MD 270 lbf; XMD 324 lbf

          - Low Temperature, flexibility, before and after heat conditioning, max, °C [°F]:

            - Before: PASS

            - After: PASS

          - Dimensional stability, max, %: NT

          - Compound stability, min, °C [°F]: PASS

          - Water absorption, max, %: N/A

          - Moisture content, max, %: N/A

          - Low temperature unrolling, max, °C [°F]: NT

        - DERBICOLOR P FR: High quality granule surfaced APP Modified Bitumen Roofing Membrane designed to act as a base or ply sheet. Meets or exceeds ASTM D6222, per ASTM D5147 test methods:

          - Thickness, min, mm [mils]: 4.1 mm [161 mils]

          - Width: 39 3/8 in [1.0 m]

          - Length: 33 ft 6in [10.2m]

          - Weight: 105lb [47.6 kg]

          - Net Coverage: 100ft2 [9m2]

          - Net mass/unit area, min, g/m2 [lbs/100 ft2]: 102 lbs/100 ft2

          - Bottom coating thickness, heat welding application products, min, mm [mils]: 45 mils

          - Peak Load at 23 ± 2°C [73.4 ± 3.6°F], MD and XMD, before and after heat conditioning, min, kN/m [lbf/in.]:

            - Before: MD 71 lbf/in; XMD 50 lbf/in

            - After: MD 67 lbf/in; XMD 50 lbf/in

          - Elongation at 23 ± 2°C [73.4 ± 3.6°F], MD and XMD at peak load, before and after heat conditioning, min, %:

            - Before: MD 49%; XMD 67%

            - After: MD 45 %; XMD 63%

          - Peak Load at -18 ± 2°C [0 ± 3.6°F], MD and XMD, min, kN/m [lbf/in.]: MD 76; XMD 61

          - Elongation at -18 ± 2°C [0 ± 3.6°F], MD and XMD, at peak load, min, %: MD 21%; XMD 15%

          - Ultimate elongation at 23 ± 2°C [73.4 ± 3.6°F], MD and XMD, min, %: MD 54 lbf/in; XMD 72 lbf/in

          - Tear Strength at 23 ± 2°C [73.4 ± 3.6°F], min, N[lbf]: MD 122 lbf; XMD 75 lbf

          - Low Temperature, flexibility, before and after heat conditioning, max, °C [°F]:

            - Before: Pass

            - After: Pass

          - Dimensional stability, max, %: MD 0.1%; XMD 0.1%

          - Compound stability, min, °C [°F]: Pass

          - Water absorption, max, %: 1.1%

          - Moisture content, max, %: 0.2 %

          - Low temperature unrolling, max, °C [°F]: Pass

    - VAPOR RETARDER, ASPHALT APPLIED:

        - DERBIBASE: High quality smooth surfaced APP Modified Bitumen Roofing Membrane designed to act as a base or ply sheet. Meets or exceeds ASTM D6509, per ASTM D5147 test methods:

          - Thickness, min, mm [mils]: 2.0 [80]

          - Width: 39 3/8 in [1.0 m]

          - Length: 66ft 5 in [20.1m]

          - Weight: 94 lb [42.6 kg]

          - Net Coverage: 200ft2 [18.6 m2]

          - Net mass/unit area, min, g/m2 [lbs/100 ft2]: [49 lbs/100 ft2]

          - Bottom coating thickness, heat welding application products, min, mm [mils]: N/A

          - Peak Load at -18 ± 2°C [0 ± 3.6°F], MD and XMD, min, kN/m [lbf/in.]:

            - MD 166 lbf/in; XMD 141 lbf/in

          - Elongation at -18 ± 2°C [0 ± 3.6°F], MD and XMD at peak load, min, %: MD 4.4 %; XMD: 4.8 %

          - Peak Load at 23 ± 2°C [73.4 ± 3.6°F], MD and XMD, before and after heat conditioning, min, kN/m [lbf/in.]:

            - Before: MD 108 lbf/in, XMD 82 lbf/in

            - After: MD 114 lbf/in, XMD 100 lbf/in

          - Elongation at 23 ± 2°C [73.4 ± 3.6°F], MD and XMD at peak load, before and after heat conditioning, min, %:

            - Before: MD 4.0 %; XMD: 4.1 %

            - After: MD 3.8 %; XMD: 4.1 %

          - Tear Strength at 23 ± 2°C [73.4 ± 3.6°F], min, N[lbf]: MD 127 lbf; XMD 103 lbf

          - Low Temperature, flexibility, before and after heat conditioning, max, °C [°F]:

            - Before: 32°F

            - After: 32°F

          - Dimensional stability, max, %: MD 0.0%; XMD: 0.0%

          - Compound stability, min, °C [°F]: 230°F

          - Water absorption, max, %: 1.2%

          - Moisture content, max, %: 0.4%

          - Low temperature unrolling, max, °C [°F]: Pass

        - DERBIBASE Ultra: High quality smooth surfaced APP Modified Bitumen Roofing Membrane designed to act as a base or ply sheet. Meets or exceeds ASTM D6509, per ASTM D5147 test methods:

          - Thickness, min, mm [mils]: 3.0mm [120 mils]

          - Width: 39 3/8 in [1.0 m]

          - Length: 49ft 6 in [15m]

          - Weight: 108 lb [48.9 kg]

          - Net Coverage: 150ft2 [13.9 m2]

          - Net mass/unit area, min, g/m2 [lbs/100 ft2]: [63 lbs/100 ft2]

          - Bottom coating thickness, heat welding application products, min, mm [mils]: 60 mils

          - Peak Load at -18 ± 2°C [0 ± 3.6°F], MD and XMD, min, kN/m [lbf/in.]:

            - MD 166 lbf/in; XMD 141 lbf/in

          - Elongation at -18 ± 2°C [0 ± 3.6°F], MD and XMD at peak load, min, %: MD 4.4 %; XMD: 4.8 %

          - Peak Load at 23 ± 2°C [73.4 ± 3.6°F], MD and XMD, before and after heat conditioning, min, kN/m [lbf/in.]:

            - Before: MD 108 lbf/in, XMD 82 lbf/in

            - After: MD 118 lbf/in, XMD 105 lbf/in

          - Elongation at 23 ± 2°C [73.4 ± 3.6°F], MD and XMD at peak load, before and after heat conditioning, min, %:

            - Before: MD 4.0 %; XMD: 4.1 %

            - After: MD 3.8 %; XMD: 4.1 %

          - Tear Strength at 23 ± 2°C [73.4 ± 3.6°F], min, N[lbf]: MD 127 lbf; XMD 103 lbf

          - Low Temperature, flexibility, before and after heat conditioning, max, °C [°F]:

            - Before: 32°F

            - After: 32°F

          - Dimensional stability, max, %: MD 0.0%; XMD: 0.0%

          - Compound stability, min, °C [°F]: 230°F

          - Water absorption, max, %: 1.2%

          - Moisture content, max, %: 0.4%

          - Low temperature unrolling, max, °C [°F]: Pass

        - PRS Glass Ply IV: High Performance fiberglass ply sheet with excellent tensile strength. Meets or exceeds ASTM D2178, Type IV, Grade N/A, per ASTM D5147 test methods:

          - Width: 36 in (.9 m)

          - Length: 180 ft (54.9 m)

          - Roll weight: 45 lb (20.4 kg)

          - Net Coverage: 487 ft2 (45.2 m2)

        - PRS Glass Ply VI: High performance fiberglass ply sheet with excellent tensile strength. Meets or exceeds ASTM D2178, Type VI, Grade N/A, per ASTM D5147 test methods:

          - Width: 36 in (.9 m)

          - Length: 180 ft (54.9 m)

          - Weight: 45 lb (20.4 kg)

          - Net Coverage: 487 ft2 (45.2 m2)

        - PRS Glass Base: High quality base or ply sheet constructed form fiberglass mat coated with oxidized asphalt. Meets or exceeds ASTM D4601, Type II, Grade N/A, per ASTM D5147 test methods:

          - Width: 36 in (.9 m)

          - Length: 108 ft (32.9 m)

          - Weight: 78.5 lb (35.6 kg)

          - Net Coverage: 291.7 ft2 (27 m2)

        - PRS Modified Base Sheet: High quality base or ply sheet constructed from fiberglass mat coated with SBS Modified Bitumen. Meets or exceeds ASTM D4601, Type II, Grade N/A, per ASTM D5147 test methods:

            - Width: 36 in (.9 m)

            - Length: 108 ft (32.9m)

            - Weight: 93 lb (42.1 kg)

            - Net Coverage: 291.7 ft2 (27 m2)

  - ACCESSORIES

    - PRIMERS:

      - ASPHALT ROOF PRIMER:  Asphalt cut-back primer.  Primer for the preparation of membrane substrates for asphalt, heat-welded, hot asphalt and PERMASTIC, solvent-based, cold adhesive-applied and cement applications.

        - Meets or exceeds ASTM D41

        - VOC content:  348 g/L

      - DERBIBASE SA PRIMER: 0 g/L VOC solvent, self-adhesive membrane primer.  Low VOC, solvent-based primer for the preparation of membrane substrates for self-adhered APP membrane and self-adhesive APP flashing applications.

      - NOTE: Primer not required for SOPREMA COLPLY EF Adhesive and SOPREMA COLPLY EF Flashing Cement applications.

    - VAPOR RETARDER ADHESIVES:

      - PERMASTIC ADHESIVE:  APP-modified bitumen membrane adhesive for use with sanded base ply and granule-surfaced Cap Sheet membranes.

        - VOC Content: 200 g/L.

        - Meets or exceeds ASTM D3019

      - SOPREMA COLPLY EF ADHESIVE: Premium, non-toxic, low odor, solvent-free, polymeric membrane adhesive for use with all SBS-modified bitumen sanded base ply and all Cap Sheet membrane applications.

a. VOC Content: 32 g/L or less VOC Content.

      - b. Meets or exceeds ASTM D7379

    - MOPPING ASPHALT

      - MOPPING ASPHALT pre-approved in writing by membrane manufacturer for use for applying the specified SBS-modified bitumen membrane.

        - Application Rate:  Solid mopping, full coverage at 23-25 lb per square and as required for specified approvals.

        - Application Temperature:  Apply asphalt at the published EVT and no less than 400(F (204(C) at the point of contact when applying the SBS-modified bitumen membrane into the asphalt.

        - The Equiviscous Temperature (EVT), the finished blowing temperature (FBT) and the flash point (FP) shall be indicated on each container.

        - Meets or exceeds ASTM D312, Type IV as listed in Table I.

    - FLASHING CEMENT

      - PERFLASH: APP-modified bitumen membrane flashing cement for use with sanded base ply flashing and granule-surfaced Cap Sheet flashing.

        - VOC Content:  165 g/L

        - Meets or exceeds ASTM D4586

    - GENERAL PURPOSE ROOFING CEMENT AND MASTIC

      - DERBIGUM 119:  Mastic.  Fiber-reinforced, roofing cement, packaged in 3- or 5-gallon pails.  General purpose roofing cement for low-slope roofing used for sealing membrane T-joints and membrane edges along terminations, transitions and at roof penetrations.

        - VOC Content:  250 g/L or less.

        - Meets or exceeds ASTM D4586, Type I, Class II.

    - GENERAL PURPOSE SEALANT

      - CHEMLINK DURALINK 50:  General purpose, paintable, gun-grade, elastomeric, polyether moisture curing sealant for sealing Kynar 500 PVDF, horizontal and vertical construction joints.

        - VOC Content:  22 g/L or less.

        - Meets or exceeds ASTM C920, Type S, Grade NS, Class 50.

        - Standard color, custom color.

    - LIQUID-APPLIED REINFORCED FLASHING SYSTEM:

      - DERBIFLASH RS 230 Flash: Catalyzed polymethyl methacrylate (PMMA) resin with polyester reinforcing fleece fabric fully embedded into the resin to form fully reinforced waterproofing membrane flashings.

        - VOC Content:  No VOC content.

        - DERBIFLASH RS 230 FLASH: Polymethyl methacrylate (PMMA) liquid resin.

        - DERBIFLASH RS CATALYST POWDER:  Reactive agent added to the PMMA liquid resin to induce curing.

        - DERBIFLASH RS FLEECE:  Polyester reinforcement fabric.

        - Color:  Flash color and finish to match Field.

- EXECUTION

  - EXAMINATION

    - Examination includes visual observations, qualitative analysis, and quantitative testing measures as necessary to ensure conditions remain satisfactory throughout the project.

    - The contractor shall examine all roofing substrates including, but not limited to: insulation materials, roof decks, walls, curbs, rooftop equipment, fixtures, and wood blocking.

    - The applicator shall not begin installation until conditions have been properly examined and determined to be clean, dry and, otherwise satisfactory to receive specified roofing materials.

    - During the application of specified materials, the applicator shall continue to examine all project conditions to ensure conditions remain satisfactory to complete the specified roofing system.

  - PREPARATION

    - Before commencing work each day, the contractor shall prepare all roofing substrates to ensure conditions are satisfactory to proceed with the installation of specified roofing materials.  Preparation of substrates includes, but is not limited to, substrate repairs, securement of substrates, eliminating all incompatible materials, and cleaning.

    - Where conditions are found to be unsatisfactory, work shall not begin until conditions are made satisfactory to begin work. Commencing of work shall indicate contractor’s acceptance of conditions.

  - PRIMER APPLICATION

    - Examine all substrates, and conduct adhesion peel tests as necessary, to ensure satisfactory adhesion is achieved.

    - Apply the appropriate specified primer to dry, compatible substrates as required to enhance adhesion of new specified materials.

    - Apply primer using brush, roller, or sprayer at the rate published on the product data sheet.

    - Asphalt Primer:  Apply ( PRS ASPHALT ROOF PRIMER primer to dry compatible masonry, metal, wood and other required substrates before applying asphalt and heat-welded membrane plies.  Primer is optional for solvent based solvent-based SBS adhesives and cements, refer to product data sheets.

    - Self-Adhesive Membrane Primer: Apply (DERBIBASE SA PRIMER) to dry, compatible substrates as required to enhance adhesion of self-adhesive membrane plies.  Ensure self-adhered membrane primer is tacky to-the-touch, but not wet.  Primer should not transfer to the finger tips when touched.

    - Project conditions vary throughout the day.  Monitor changing conditions, monitor the drying time of primers, and monitor the adhesion of the membrane plies.  Adjust primer and membrane application methods as necessary to achieve the desired results.

    - Primer is not required for SOPREMA COLPLY EF Adhesive and SOPREMA COLPLY EF Flashing Cement.

  - HEAT WELDING

    - The Contractor is responsible for project safety.  Where conditions are deemed unsafe to use open flames, manufacturer’s alternate membrane application methods shall be used to install SBS modified bitumen membrane and flashings. Acceptable alternate installation methods include hot asphalt, cold adhesive-applied, self-adhered membranes and mechanically fastened plies.  Hot-air welding equipment may be used in lieu of roof torches to seal membrane side and end laps where heat welding the laps is necessary.   Refer to NRCA CERTA, local codes and building owner’s requirements for hot work operations.

    - Single or multi-nozzle, hand-held propane roof torches shall be used to install heat-welded plies. Multi-nozzle carts (dragon wagons) may also be utilized to install plies.  Seven (7) nozzle carts are recommended for more uniform heat application in lieu of five (5) nozzle carts.

  - MEMBRANE ADHESIVE APPLICATION

    - The ambient temperature shall be above 50(F (10(C), and the adhesive temperature shall be a minimum of 70(F (21(C) at the point of membrane application.

    - To ensure the adhesive is applied at 70(F (21(C), during cold weather, drums and 5 gallon pails shall be stored in heated areas.  Drums and 5 gallon pails exposed to cold temperature on the roof shall be provided with heaters when necessary to ensure the minimum application temperature is maintained.

    - Priming substrates is optional when solvent-based membrane adhesives are used.  Primer may be applied to reduce adhesive consumption rates for some absorptive substrates.

    - PERMASTIC ADHESIVE may be applied using a 3/16 – 3/8 inch notched squeegee, brush or spray equipment.

    - SOPREMA COLPLY EF ADHESIVE may be applied using a 3/16 – 3/8 inch notched squeegee or brush. SOPREMA COLPLY EF ADHESIVE is not spray-applied.

    - Apply adhesive to clean, dry and prepared compatible substrates as required to ensure full adhesion.

    - Follow the adhesive product data sheet requirements for application rates.

    - Apply a uniform application of membrane adhesive at the application rate published on the product data sheet.

    - Apply 1-1/2 to 2 gallons per square between membrane plies.  The application rate is 2 to 2-1/2  gallons per square or more over absorptive substrates and over granule surfaces.  Refer to manufacturer’s product data sheet, and adjust application rate based upon surface conditions.

    - PARTIALLY ADHERED (RIBBON-APPLIED) ADHESIVE APPLICATION:

1. 	SOPREMA COLPLY EF ADHESIVE shall be applied in ½ to ¾ in wide ribbons to the deck surface.

2. 	Apply COLPLY EF in uniformly spaced ribbons, 6 in on centers maximum spacing. Spacing shall be reduced to 4 in on centers in roof perimeters and corners where required for wind uplift ratings or manufacturer’s warranty.

3. 	Ribbons shall be installed to ensure partial attachment where necessary to promote relief of vapor pressure that may occur between the substrate and underside of the ply.

    - Install the APP membrane ply before the adhesive begins to skin over.  Once adhesive skins over, the membrane ply will not adhere.

  - MOPPING ASPHALT APPLICATION

    - Mopping asphalt manufacturer and type shall be preapproved by the manufacturer.

    - Refer to mopping asphalt supplier published values for Softening Point, Minimum Flash Point (FP), Finished Blowing Temperature (FBT) and Equiviscous Temperature (EVT).

    - Refer to the Softening Point for maximum Roof Slope applications. The maximum recommended roof slope for asphalt built-up roofing felts is 3/4:12.  Contact the manufacturer for special requirements necessary to prevent membrane slippage for roof slopes that exceed 3/4:12.

    - To avoid risk of fire do not heat asphalt at or above the Flash Point temperature.

    - The EVT is the temperature at which the mopping asphalt viscosity is 125 centistokes.

    - Apply mopping asphalt within +/- 25(F (14(C) of the published EVT to obtain the nominal 23 to 25 pounds per square coverage rate.

    - Refer to the EVT provided by the asphalt supplier.  Typically, the Type III asphalt application temperature should be within 365 to 435(F (185 to 224(C) and Type IV asphalt application temperature should be within 400 to 475(F (204 to 246(C) at the point of application when installing roofing materials into the hot asphalt.

    - For SBS modified bitumen vapor retarder applications; ASTM D312 Type IV asphalt is required.

    - For SBS modified bitumen plies, the asphalt temperature shall not fall below 400(F (204(C) at the point of membrane contact when installing the SBS membrane into the hot asphalt.

    - The contractor shall monitor asphalt application temperature, and shall record the temperature during application.

  - FLASHING CEMENT APPLICATION

    - The ambient temperature shall be above 50(F (10(C), and the flashing cement temperature shall be a minimum of 70(F (21(C) at the point of membrane application.

    - To ensure the flashing cement is applied at 70(F (21(C), during cold weather, pails shall be stored in heated areas.  Pails exposed to cold temperature on the roof shall be provided with heaters when necessary to ensure the minimum application temperature is maintained

    - Priming substrates is optional when solvent-based membrane adhesives are used.  Primer may be applied to reduce adhesive consumption rates for some absorptive substrates.

    - PERFLASH FLASHING CEMENT may be applied using ¼ inch notched trowel. Apply 2.0 – 2.5 gallons per square to each surface.  Primer may be used to reduce consumption of solvent based flashing cement.

    - Application rates vary based on substrate porosity and roughness.

  - MASTIC AND GENERAL PURPOSE ROOFING CEMENT APPLICATION

    - Apply DERBIGUM 119 general purpose mastic and roofing cement to seal drain leads, metal flanges, seal along membrane edge at terminations, and where specified and required in detail drawings.

    - Do not use general purpose mastics and roofing cement where flashing cement applications are required.  Do not use mastics and roofing cement beneath modified bitumen membrane and flashing plies.

    - Apply general purpose mastic and elastic roofing cement using caulk gun, or notched trowel at 2.0 – 2.5 gallons per square on each surface.  Application rates vary based on substrate porosity and roughness.  Tool-in as necessary to seal laps

  - HEAT-WELDED, FULLY ADHERED VAPOR RETARDER APPLICATION

    - Follow material product data sheets and published general requirements for installation instructions.

    - Ensure environmental conditions are safe and satisfactory, and will remain safe and satisfactory, during the application of the heat-welded vapor retarder membrane.

    - Ensure all primers are fully dry before beginning heat-welding operations.

    - Unroll membrane onto the roof surface and allow time to relax prior to heat welding.

    - Starting at the low point of the roof, lay out the membrane to ensure the plies are installed perpendicular to the roof slope, shingled to prevent back-water laps.

    - Ensure all roofing and flashing substrates are prepared and acceptable to receive the heat-welded membrane.

    - Cut membrane to working lengths and widths to conform to rooftop conditions, and lay out to always work to a selvage edge.

    - Ensure specified side-laps and end-laps are maintained.  End-laps should be staggered 3 ft apart.

    - Direct roof torch on the roll as necessary to prevent overheating and damaging the membrane and substrates.

    - As the membrane is unrolled, apply heat to the underside of the membrane until the plastic burn-off film melts away.   Continuously move the torch side-to-side across the underside of the roll to melt the bitumen on the underside of the sheet, while continuously unrolling the membrane.

    - While unrolling and heating the sheet, ensure a constant flow hot bitumen approximately ¼ to 1/2 in flows ahead of the roll as it is unrolled, and there is 1/8 to 1/4 in bleed out at all laps.

    - Adjust the application of heat to the underside of the membrane and to substrate as required for varying substrates and environmental conditions.

    - At end-laps, cut a 45-degree dog-ear away from the selvage edge, or otherwise ensure the membrane is fully heat-welded watertight at all T-joints.

    - Each day, physically inspect all side and end-laps, and ensure the membrane is sealed watertight.  Where necessary, use a torch or hot-air welder and a clean trowel to ensure all laps are fully sealed.

    - Inspect the installation each day to ensure the plies are fully adhered.  Repair all voids, wrinkles, open laps and all other deficiencies.

  - SELF-ADHESIVE VAPOR RETARDER APPLICATION

    - Follow material product data sheets and published general requirements for installation instructions.

    - Ensure environmental conditions are satisfactory, and will remain satisfactory, during the application of the self-adhesive membrane.

    - Unroll membrane onto the roof surface and allow time to relax prior to installing the membrane.

    - Starting at the low point of the roof, lay out the membrane to ensure the plies are installed perpendicular to the roof slope, shingled to prevent back-water laps.

    - Ensure all substrates are prepared and acceptable to receive the self-adhesive membrane.

    - Ensure primer is tacky to-the-touch, but not wet.  Primer should not transfer to the finger tips when touched.  Do not proceed if primer is wet or becomes fully dry and dirty.  If primer becomes fully dry, dirty and looses all tack, re-prime the substrate as necessary to achieve membrane adhesion.

    - Cut rolls to working lengths and widths to conform to rooftop conditions, and lay out to always work to a selvage edge.

    - Ensure membrane side-laps end-laps are maintained.

    - Peel the release film from the underside of the membrane. Press and adhere the leading edge of the membrane to the substrate, but leaving the 6 in end-lap un-adhered in order to heat weld the end-lap.

    - As the release film is peeled away, use a weighted roller to firmly set the sheet in place.  Ensure full contact is made between the ply and the substrate for full adhesion.  Use a hand-roller to roll-in vertical applications and confined areas to firmly apply pressure.

    - At 6 in end-laps, cut a 45-degree dog-ear away from the 3 in selvage edge, or otherwise ensure the membrane is fully heat-welded watertight at all T-joints.

    - Offset self-adhered end-laps 3 ft

    - Each day, physically inspect all side and end-laps, and ensure the membrane is sealed watertight.  Where necessary, use a torch or hot-air welder and a clean trowel to ensure all laps are fully sealed.

    - Inspect the installation each day to ensure the plies are fully adhered.  Repair all un-adhered voids, wrinkles, open laps and all other deficiencies.

  - COLD ADHESIVE-APPLIED VAPOR RETARDER APPLICATION

    - Follow material product data sheets and published general requirements for installation instructions.

    - Ensure environmental conditions are satisfactory, and will remain satisfactory, during the application of the membrane adhesive and membrane plies.

    - Unroll membrane onto the roof surface and allow the membrane to relax prior to installing the membrane.

    - Re-roll the membrane in order for the plies to be rolled into the adhesive while ensuring the specified side and end-laps are maintained

    - Starting at the low point of the roof, lay out the membrane to ensure the plies are installed perpendicular to the roof slope, shingled to prevent back-water laps.

    - Cut rolls to working lengths and widths to conform to roof conditions, and lay out to always work to a selvage edge.

    - Ensure all substrates are prepared as necessary, and all substrates are acceptable to receive the specified adhesive and membrane.

    - Install the specified membrane adhesive ahead of the membrane application.  Do not allow the adhesive to skin-over before the membrane is applied into the adhesive. The membrane will not adhere where adhesive has skinned over.

    - Where laps are adhered using membrane adhesive, apply sufficient adhesive coverage to ensure 1/8 to 1/4 in bleed-out is present at all laps.

    - Once set in place, ensure specified side-laps and end-laps are maintained.

    - At end-laps, cut a 45-degree dog-ear away from the selvage edge for all T-joints.

    - For low-slope areas where the roof slope falls below 1/4 in per foot, and where otherwise specified, leave all membrane side and end-laps dry in order to hot-air weld or torch all laps watertight.  Embed granules, where present, when heat welding sheets.

    - Use a follow tool, weighted roller or broom the leading edge of the membrane to the substrate, working forward and outward as necessary to remove wrinkles.  Avoid walking over the membrane during application.

    - Each day, physically inspect all side and end-laps, and ensure the membrane is sealed watertight.  Where necessary, use a torch or hot-air welder and a clean trowel to ensure all laps are fully sealed.

    - Inspect the installation each day to ensure the plies are adhered.  Repair all voids, wrinkles, open laps and all other deficiencies.

  - ASPHALT-ADHERED  MODIFIED BITUMEN VAPOR RETARDER APPLICATION

    - Follow manufacturer’s material product data sheets and published general requirements for installation instructions.

    - Ensure environmental conditions are satisfactory, and will remain satisfactory, during the application of the mopping asphalt and membrane plies.

    - Unroll the membrane onto the roof surface. Allow modified bitumen membrane plies to relax prior to installing the membrane.

    - Starting at the low point of the roof, lay out the membrane to ensure the plies are installed perpendicular to the roof slope, shingled to prevent back-water laps.  Where strapping is preferred, refer to membrane layout guidelines.

    - Cut rolls to working lengths and widths as required to conform to rooftop conditions.  Cut membrane plies as necessary to always work to a selvage edge.

    - Ensure all roofing and flashing substrates are prepared and primed as necessary, and all substrates are acceptable to receive the specified asphalt and membrane.

    - Re-roll the membrane in order for the plies to be rolled into the hot asphalt while ensuring the specified side and end-laps are maintained.

    - Mop a uniform application of hot asphalt within +/- 25(F (14(C) of the Equiviscous Temperature (EVT).  Apply sufficient asphalt coverage to ensure 1/8 to 1/4 inch bleed-out is present beyond all laps.  Prevent excessive asphalt bleed-out on the SBS ply surface.

    - The asphalt temperature shall not fall below the minimum EVT temperature range at the point of membrane contact when rolling the sheet into the hot asphalt.

    - The asphalt application temperature should be monitored at the point of membrane application, and recorded during application.

    - At 6 inch end-laps, cut a 45 degree dog-ear away from the 3 inch selvage edge for all T-joints.

    - Broom the membrane to the substrate, working forward to the end of the roll as necessary to remove wrinkles and voids to ensure full adhesion.  Avoid walking over the membrane during application.

    - Each day, physically inspect all side and end-laps, and ensure the membrane is sealed watertight.

    - Inspect the installation each day to ensure the plies are fully adhered.  Repair all voids, wrinkles, open laps and all other deficiencies.

  - ASPHALT BUR VAPOR RETARDER

    - Follow material product data sheets and published general requirements for installation instructions.

    - Ensure environmental conditions are satisfactory, and will remain satisfactory, during the application of the mopping asphalt and membrane plies.

    - Where applicable, install red rosin paper or other separator sheet over the roof deck to prevent asphalt from entering the building and to prevent asphalt bleed-through to the roof deck.

    - Starting at the low point of the roof, lay out the membrane to ensure the plies are installed perpendicular to the roof slope, shingled to prevent back-water laps.

    - Ensure all roofing substrates are primed and prepared as necessary, and all substrates are acceptable to receive the specified asphalt and membrane.

    - Apply mopping asphalt within +/- 25(F (14(C) of the published EVT to obtain the nominal 23 to 25 pounds per square coverage rate.

    - Refer to the EVT provided by the asphalt supplier.  Typically, the Type III asphalt application temperature should be within 365 to 435(F (185 to 224(C) and Type IV asphalt application temperature should be within 400 to 475(F (204 to 246(C) at the point of application when rolling the felt into the hot asphalt.

    - The application temperature shall be monitored and recorded during application.

    - TWO (2) PLY BUILT-UP VAPOR RETARDER APPLICATION:

      - First start at the low edge of the roof by installing a felt cut 18 inches wide, installed along the low edge.

      - Second install a full 36 inch wide felt, installed along the same low edge of the roof.

      - Next install a full 36 inch wide felt, installed 19 inches over the second felt (17 inches from the roof edge).

      - Each of the following felts should also be installed 19 inches over the preceding felt, producing the same 17 inch exposure.

      - Follow the lay-lines on the felts or snap chalk lines as required to maintain consistent 2-ply membrane coverage, with 2 inch side laps and 4 inch end laps.

    - THREE (3) PLY BUILT-UP VAPOR RETARDER APPLICATION:

      - First start at the low edge of the roof by installing a felt cut 12 inches wide, installed along the low edge.

      - Second install a felt cut 24 inches wide, installed along the same low edge of the roof.

      - Third install a full 36 inch wide felt, installed along the same low edge of the roof.

      - Next install a full 36 inch wide felt, installed 24-2/3 inches over the third felt (11-1/8 inches from the roof edge).

      - Each of the following felts should be installed 24-2/3 inches over the preceding felt, producing the same 11-1/8 inch exposure.

      - Follow the lay-lines on the felts or snap chalk lines as required to maintain consistent 3-ply membrane coverage, with 2 inch side laps and 4 inch end laps.

    - FOUR (4) PLY BUILT-UP VAPOR RETARDER APPLICATION: :

      - First start at the low edge of the roof by installing a felt cut 9 inches wide, installed along the low edge.

      - Second install a felt cut 18 inches wide, installed along the same low edge of the roof.

      - Third install a felt cut 27 inches wide, installed along the same low edge of the roof.

      - Fourth install a full 36 inch wide felt installed along the same low edge of the roof.

      - Next install a full 36 inch wide felt, installed 27-1/2 inches over the fourth felt (8-1/2 inches from the roof edge).

      - Each of the following felts should be installed 27-1/2 inches over the preceding felt, producing the same 8-1/2 inch exposure.

      - Follow the lay-lines on the felts or snap chalk lines as required to maintain consistent 4-ply membrane coverage, with 2 inch side laps and 4 inch end laps.

    - Carefully squeegee the ply felts in place, working forward to the end of the roll as necessary to remove wrinkles and voids to ensure full adhesion.

    - Avoid walking over the membrane during application to prevent displacing asphalt between felts.  Allow the asphalt to cool sufficiently before walking over the new membrane.

    - Inspect the installation each day to ensure the plies are fully adhered.  Repair all voids, wrinkles, open laps and all other deficiencies.

    - Do not leave built-up membrane felts exposed overnight. Each day, squeegee a thin glaze coating of asphalt over the built-up membrane surface, or install the specified protective surfacing before the end of each work day.

    - Do not phase built-up roofing felt applications.  Install the total number of specified built-up roofing felts each day.

  - LIQUID-APPLIED, PMMA MEMBRANE AND FLASHING SYSTEM APPLICATION DERBIFLASH RS

    - Refer to manufacturer’s details drawings, product data sheets and published general requirements for application rates and specific installation instructions.

    - Pre-cut DERBIFLASH RS FLEECE polyester reinforcing fleece to conform to roof terminations, transitions and penetrations being flashed.  Ensure a minimum 2 in overlap of fleece at side and end-laps. Ensure the completed liquid-applied flashing membrane is fully reinforced.

    - Apply the base coat of catalyzed  DERBIFLASH RS resin onto the substrate using a brush or roller, working the material into the surface for complete coverage and full adhesion.

    - Immediately apply the  DERBIFLASH RS FLEECE reinforcing into the wet base coat of resin.  Using a brush or roller, work the  DERBIFLASH FLEECE reinforcing fabric into the wet resin while applying the second coat of catalyzed  DERBIFLASH RS resin to completely encapsulate the fleece.

    - Refer to reinforced, polymethyl-methacrylate (PMMA) specification section and application instructions, details drawings, product data sheets and published general requirements for installation instructions.

  - CLEAN-UP

    - Clean-up and properly dispose of waste and debris resulting from these operations each day as required to prevent damages and disruptions to operations.

END OF SECTION